## Slide 1
Water
Treatment

## Slide 2: Water Softening methods
1. Lime soda
a) Batch process
b) continuous process
- Cold lime-soda
- Hot lime-soda
2. Zeolite (permutit) process
3. Ion-exchange and Mixed bed ion-exchange process

## Slide 3: Lime – Soda Process
a. Reaction of permanent calcium:
Ca2+ + Na2CO3 CaCO3 + 2Na+
b. Reactions of permanent magnesium:
Mg2+ + Ca(OH)2 Ca2+ + Mg(OH)2
Ca2+ + Na2CO3 CaCO3 + 2Na+
c. Reaction of HCO3- (ex-Na2CO3):
2 HCO3- + Ca(OH)2 CaCO3 + H2O + CO32-
d. Reaction of Ca(HCO3)2 :
Ca(HCO3)2 + Ca(OH)2 2 CaCO3 + 2 H2O
e. Reaction of Mg(HCO3)2 :
Mg(HCO3)2 + 2 Ca(OH)2 2 CaCO3 + 2 H2O + Mg(OH)2

## Slide 4: Lime – Soda Process
f. Reaction of CO2:
CO2 + Ca(OH)2 CaCO3 + H2O
g. Reaction of H+:
2 H+ + Ca(OH)2 Ca2+ + 2 H2O
Ca2+ + Na2CO3 CaCO3 + 2 Na+
h. Reactions of coagulants:
i) Reaction of FeSO4:
Fe2+ + Ca(OH)2 Fe(OH)2 + Ca2+
Fe(OH)2 + H2O + O2 2 Fe(OH)3
Ca2+ + Na2CO3 CaCO3 + 2 Na

## Slide 5
ii) Reactions of Aluminium sulphate (Al2(SO4)3 :
2 Al3+ + 3 Ca(OH)2 2 Al(OH)3 + 3 Ca2+
3 Ca2+ + 3 Na2CO3 3 CaCO3 + 6 Na+
iii) Reactions of sodium aluminate (NaAlO2):
NaAlO2 + H2O Al(OH)3 + NaOH
Lime [Ca(OH)2]requirement :
74 Temp. Ca2+ + 2 temp. Mg2+ + Perm(Mg2+ + Al3+ + Fe2+) + CO2 + H+ + HCO3-
- NaAlO2
B. Soda[Na2CO3] requirement :
106 Perm. (Ca2+ + Mg2+ Fe2+ + Al3+) + H+ - HCO3-
{
100
{
{
{
100

## Slide 6
Lime –Soda process equipment

## Slide 7
Hot lime-soda process consists of three parts:
Reaction tank to mix all ingredients
b) Conical sedimentation vessel where the sludge settles down
c) Sand filter where sludge is completely removed
Advantages of hot lime-soda process:
The precipitation reactions are almost complete
Reactions takes place faster
Sludge settles down rapidly; No coagulant is needed
Dissolved gases (which may cause corrosion) are removed
Viscosity of soft water is lower, hence filtered easily
Residual hardness is low compared to cold lime-soda process
Lime –Soda process equipment

## Slide 8: Advantages & disadvantages of lime-soda process:
Advantages of Lime – soda process:
Economical
Process improves the corrosion resistance of water
Mineral content of water is reduced
pH of water raises thus reducing content of pathogenic bacteria
No skilled labour is required
Disadvantages of Lime – soda process:
Huge amount of sludge is formed and its disposal is difficult
Due to residual hardness, water is not suitable for high pressure boilers

## Slide 9: Permutit or Zeolite Process
Zeolite is hydrated sodium aluminium silicate having a general formula, Na2OAl2O3.xSiO2.yH2O.
It exchanges Na+ ions for Ca2+ and Mg2+ ions.
Common Zeolite is Na2OAl2O3.3SiO2.2H2O known as natrolite.
Artificial zeolite used for water softening is Permutit.
They are prepared by heating china clay, feldspar and soda ash (hydrated aluminium silicate), feldspar (KAlSi3O8-NaAlSi3O8 – CaAl2Si2O8) are a group of rock-forming tectosilicate minerals which make up as much as 60% of the earth’s crust) and soda ash (Na2CO3)

## Slide 10: Zeolite process
Method of softening:
Na2Ze + Ca(HCO3)2 2 NaHCO3 + CaZe
Na2Ze + Mg(HCO3)2 2 NaHCO3 + MgZe
Na2Ze + CaSO4 2 Na2SO4 + CaZe
Na2Ze + CaCl2 2 NaCl + CaZe
Regeneration of Zeolite:
CaZe (or) MgZe + 2 NaCl Na2Ze + CaCl2 or MgCl2
Brine solution

## Slide 11: Zeolite process equipment diagram

## Slide 12: Zeolite Process
Advantages:
  Residual hardness of water is about 10 ppm only
  Equipment is small and easy to handle
  Time required for softening of water is small
  No sludge formation and the process is clean
  Zeolite can be regenerated easily using brine solution
  Any type of hardness can be removed without any modifications to the process
Disadvantages:
  Colored water or water containing suspended impurities cannot be used without filtration
  Water containing acidic pH cannot be used for softening since acid will destroy zeolite.

## Slide 13: Ion-Exchange Process
Ion-exchange resins are cross linked long chain polymers with
microporous structure.
Cation exchange resins will exchange cations with H+.
Anion exchange resins will exchange anions with OH-.
Functional groups present are responsible for ion-exchange
properties.
Acidic functional groups (-COOH, -SO3H etc.) exchange H+ for
cations &
Basic functional groups (-NH2, =NH etc.) exchange OH- for anions.

## Slide 14: Ion-Exchange Process
A. Cation-exchange Resins(RH+):
- Styrene divinyl benzene copolymers
- When sulphonated, capable of exchange H+

## Slide 15: Ion Exchange Process
B. Anion-exchange resins (R’OH):
- Styrene divinyl benzene copolymers or amine formaldehyde copolymers with NH2,
QN+, QP+, QS+, groups.
- On alkali treatment, capable of exchange of OH-
Anion Exchange resin

## Slide 16: Ion Exchange Process
The Process of Ion-exchange is:
2 RH+ + Ca2+/Mg2+ R2Ca2+/R2Mg2+ + 2 H+ (Cation exchange)
R’OH- + Cl- R’+ Cl- + OH- (anion exchange)
2 R’OH- + SO42- R’2 SO42- + 2 OH- (anion exchange)
2 R’OH- + CO32- R’2 CO32- + 2 OH- (anion exchange)
Finally,
H+ + OH- H2O
Regeneration of exhausted resins:
Saturated resins are regenerated by treating with strong mineral acid or alkali respectively
R2Ca2+/R2Mg2+ + 2H+ 2 RH+ + Ca2+/Mg2+ (Strong acid)
(washings)
R’2 SO42- + 2 OH- 2 R’OH- + SO42- (Strong base)
(washings)

## Slide 17
Ion-exchange process
Note: Hard water should be first passed through the cation exchanger and then
Anion exchanger to avoid hydroxides of Ca2+ and Mg2+ getting formed

## Slide 19: Mixed bed ion-exchanger
Deminaralised
water
Mixed
ionizer
bed
Mixed ionizer
bed
Exhausted mixed
ionizer bed
Cation exchanger
(higher density)
Anion exchanger
(low density)
NaOH
H2SO4
Washings to
sink
Comp.
air
Backwash
water
Contains intimate mixture of cation and anion exchangers
Water is in contact for a no. of times with the two exchangers alternatively
Raw water
inlet

## Slide 20: Advantages & Disadvantages of ion-exchange process
Advantages:
- Can be used for highly acid and highly alkaline water
- Residual hardness of water is as low as 2 ppm.
- Very good for treating water for high pressure boilers
Disadvantages:
  - Expensive equipment and chemicals
  - Turbidity of water should be < 10 ppm. Otherwise output will
  reduce; turbidity needs to be coagulated before treatment.
  - Needs skilled labour

## Slide 21: Specifications of different materials in drinking water (ICMR and WHO)
S.No. | Parameter/Material | WHO Standards/ppm | ICMR/BIS Standards/ppm
1 | Colour | Clear | Clear
2 | Odour | Pleasant | Pleasant
3 | Turbidity | 2.5 | 2.5
4 | pH | 6.0 – 8.5 | 6.0 – 8.5
5 | TDS | 300 | 500
6 | Total Hardness as CaCO3 | 200 | 300
7 | Calcium | 75 | 75
8 | Chlorides | 200 | 200
9 | Sulphates | 200 | 200
10 | Fluoride | 0.5 | 1.0
11 | Mercury | 0.006 | 0.001
12 | Cadmium | 0.003 | 0.01
13 | Arsenic | 0.01 | 0.02
14 | Chromium as hexavalent | 0.01 | 0.1
15 | Lead | 0.01 | 0.01
16 | E.Coli | No colony Should be present in 100 mL water | No colony Should be present in 100 mL water

## Slide 22: Water treatment for municipal supply
Sedimentation
Lakes/Reservoirs/Rivers
Storage tanks
Flocculation & Clarification
Coagulation
Filtration
Disinfection
Storage in closed containers
Supply through pipelines
Removes dirt and other particles suspended in water. Alum and other chemicals are added for coagulation through floc
Heavy particles (floc) settle to the bottom and clear water goes for filtration
Multilayer filtration using sand, gravel and charcoal
Calculated amount of chlorine is added

## Slide 23: Domestic water purification system

## Slide 24
Candles

## Slide 25: Disinfection Methods
Disinfection methods used for disinfecting water for drinking purpose are
- Ultrafiltration
- UV treatment
- Ozonolysis
- Reverse Osmosis

## Slide 26: Water purification by Filtration process
The green arrow indicates that the particle is small enough to pass through the filter, whereas the deflected orange arrow indicates that the filter blocks the particle from passing through the filter.

## Slide 27: Different filtration processes
Ultrafiltration:
An ultrafiltration filter has a pore size around 0.01 micron.
A microfiltration filter has a pore size around 0.1 micron, so when water undergoes microfiltration, many microorganisms are removed, but viruses remain in the water. Ultrafiltration would remove these larger particles, and may remove some viruses.
Neither microfiltration nor ultrafiltration can remove dissolved substances unless they are first adsorbed (with activated carbon) or coagulated (with alum or iron salts).
Nanofiltration
A nanofiltration filter has a pore size around 0.001 micron.
Nanofiltration removes most organic molecules, nearly all viruses, most of the natural organic matter and a range of salts.
Nanofiltration removes divalent ions, which make water hard, so nanofiltration is often used to
soften hard water.
C. Reverse osmosis
Reverse osmosis filters have a pore size around 0.0001 micron.
After water passes through a reverse osmosis filter, it is essentially pure water. In addition to removing all organic molecules and viruses, reverse osmosis also removes most minerals that are present in the water.
Reverse osmosis removes monovalent ions, which means that it desalinates the water.

## Slide 29: Reverse Osmosis
When two solutions of unequal concentrations are separated by a Semipermeable membrane, solvent will flow from lower conc. to higher conc. due to osmotic pressure
This phenomenon can be reversed by making the solvent to flow in the opposite direction by applying hydrostatic pressure on the concentrated side (Reverse Osmosis)
In reverse osmosis, pressure of 15-40 kg/cm2 is applied on the contaminated water compartment.
The water gets forced through the semipermeable membrane leaving behind the dissolved solids.
Thus water is separated from the contaminants rather than removing contaminants from water.
Both ionic and non-ionic impurities as well as colloidal impurities are left behind.
This process is also called as “Super-filtration” or “Hyper-filtration”

## Slide 30: Advantages of Reverse Osmosis
Advantage is in removing ionic, non-ionic, colloidal and high molecular wt. organic matter.
It removes colloidal silica (which is not removed during demineralisation)
Cost is only the replacement cost of membranes (life is 2 years)
Membrane replacement is fast and hence uninterrupted water supply can be ensured
Because of the above reasons this process is being adopted for converting sea water into potable water and for high pressure boilers.
It can be used as desalination process for removing salt from sea water.

## Slide 31: Desalination of brackish water
Water containing dissolved salts with a peculiar salty (brackish) taste is brackish water
The process of removing common salt from water is desalination
Electrodialysis consists of a large container with two membrane separators, one
permeable to positive ions and the other permeable to negative ions.
In the outer compartments anode and cathode are arranged to pass DC Voltage.
When DC voltage/current is passed through the cell, Na+ will move towards cathode
and Cl- will move towards anode through the membrane.
Hence, the concentration of salt decreases in the middle compartment and increases
in the side compartments.
Water from the middle compartment is collected and this water is desalinated water.

## Slide 32: Electrodialysis diagram
For efficient separation, ion-selective membranes are used which selectively allow cations or anions to pass through them.

## Slide 33: Electrodialysis cell
Electrodialysis cell consists of Large number of pairs of
rigid Plastic membranes.
Saline water at a pressure of 5-6 kg/cm2 is passed
through the membrane pairs.
DC current is applied
perpendicular to the direction of water flow.
Advantages are:
Unit is compact and installation is economical
Best suited if electricity is
available.